OPP-TB-253519.050

Control Valves

Energy Valve Operation

Background

“Energy Valves” are a type of Belimo actuator that has an integral flow meter and differential temperature sensors that measure and maintain an appropriate water-side temperature differential independent of the control system output.

In a typical setup, the control system will send a 0-10V (or 2-10V) signal to the control valve to maintain a discharge air setpoint.  If the design water-side delta-T is not met (typically 12 degrees), the energy valve will take over control via the “delta-T manager” until the delta-T is met.  This ignores the output from the control system.

This setup should be reflected in the control system, however, direct connection to the Ethernet connection on the valve may be required to view all valve settings.

Diagnosis

Energy Valves are easily identified visually, even through insulation, due to the additional orange control box located adjacent to the actuator, and supply water temperature sensor lead.

The control system should have a graphic that notifies you when the energy valve has taken over local control, as well as a link to view all available control points within the valve logic.

Corrective Action

If the ACF is not maintaining DAT, and the valve control is enabled, you must turn-off the delta-T manager via the control system or by directly connecting to the valve by the following procedure:

Important notes, read prior to connection:

- The static IP address located in the valve software must not be changed.  If this value is modified, the valve connection will be lost, and the unit must be sent back to Belimo for refurbishment.

- The only BAS connection value that should be modified is the device ID number.  The Environment Systems Administrator (EAS, currently Paul Scanlon) designates the Device ID number. Any new installations or modifications to the Device ID number must be coordinated with the EAS.

- The delta-T manager is an on-board control algorithm that does not utilize information or PID tuning from the control system.  Do not modify the control PID loop when delta-T management is enabled.

- DO NOT CHANGE THE USER NAME, PASSWORD, OR IP ADDRESS.  THIS WILL RENDER THE VALVE INACCESSIBLE.

Device Connection Quick Reference (Windows 7, XP is similar):

- Connect the Ethernet cable directly to the valve port.

- Open the Windows Control Panel

- Select “Network and Internet”

- Select “Network and Sharing Center”

- Select “Change Adapter Settings” from the left-left hand menu

- Right-Click “Local Area Connection”, select “Properties”

- In the new window, select “Internet Protocol Version 4 (TCP/IPv4)”, and click on the “Properties Button”

- Select the “Use the following IP Address” radio button.

- Enter 192.168.0.200 for the IP Address and 255.255.255.0 for the Subnet Mask.

- Click “OK”

- Open Internet Explorer, enter the address:  http://192.168.0.10:8080/index.html

- The user name is “admin”, the password is “tlnsg”

- REMEMBER TO CHANGE THE IPv4 SETTING TO “Automatically Obtain IP Address” WHEN FINISHED, OR YOU WON’T BE ABLE TO CONNECT TO ETHERNET ANYWHERE ELSE.

Complete Valve Instructions are attached hereto as of the last revision date listed below.  Current valve information is available at www.belimo.com.

Publisher: Penn State University, Office of Physical Plant, Energy and Engineering Division, Engineering Services

Editor: Stephen Oskin, Continuous Commissioning Engineer, Ph: (814) 867-4715, email: seo110@psu.edu

Last Revision: March 8, 2013